BEFORE THE

GEORGIA PUBLIC SERVICE COMMISSION

| IN THE MATTER OF: GEORGIA POWER COMPANY’S FIFTH SEMI-ANNUAL VOGTLE CONSTRUCTION MONITORING REPORT | DOCKET NO.: 29849 |
| --- | --- |

PUBLIC DISCLOSURE

|  | DIRECT TESTIMONY |  |
| --- | --- | --- |
|  | AND EXHIBITS |  |
|  | OF |  |
|  | WILLIAM R. JACOBS, JR., PhD. |  |

ON BEHALF OF THE

GEORGIA PUBLIC SERVICE COMMISSION

PUBLIC INTEREST ADVOCACY STAFF

December 2, 2011

Table of Contents

I.	INTRODUCTION	1

II.	Description of Construction Monitoring Activities	3

III.	Project Status	5

IV.	OTHER Issues Potentially Impacting Project Schedule

AND/OR COST	16

V	Verification and Approval of Costs	188

Exhibits:

STF-WRJ-1	Resume of William R. Jacobs, Jr., Ph.D.

# I.	INTRODUCTION

Q.	PLEASE STATE YOUR NAME, TITLE AND BUSINESS ADDRESS.

A.	My name is William R. Jacobs, Jr., Ph.D.  I am a Vice President of GDS Associates, Inc.  My business address is 1850 Parkway Place, Suite 800, Marietta, Georgia, 30067.

Q.	DR. JACOBS, PLEASE SUMMARIZE YOUR EDUCATIONAL BACKGROUND AND EXPERIENCE.

A.	I received a Bachelor of Mechanical Engineering in 1968, a Master of Science in Nuclear Engineering in 1969 and a Ph.D. in Nuclear Engineering in 1971, all from the Georgia Institute of Technology.  I am a registered professional engineer and a member of the American Nuclear Society.  I have more than thirty years of experience in the electric power industry including more than twelve years of nuclear power plant construction and start-up experience. I have participated in the construction and start-up of seven nuclear power plants in this country and overseas in management positions including start-up manager and site manager.  As a loaned employee to the Institute of Nuclear Power Operations (“INPO”), I participated in the Construction Project Evaluation Program, performed operating plant evaluations and assisted in development of the Outage Management Evaluation Program.  Since joining GDS Associates, Inc. in 1986, I have participated in rate case and litigation support activities related to power plant construction, operation and decommissioning.  I have evaluated nuclear power plant outages at numerous nuclear plants throughout the United States.  I served on the management committee of Plum Point Unit 1, a 650 Megawatts Electric (“MWe”) coal fired power plant under construction near Osceola, Arkansas.  As a member of the management committee, I assisted in providing oversight of the Engineering, Procurement and Construction (“EPC”) contractor for this project.  My resume is included in Exhibit STF-WRJ-1.

Q.	DR. JACOBS, WHAT IS THE NATURE OF YOUR BUSINESS?

A.	GDS Associates, Inc. (“GDS”) is an engineering and consulting firm with offices in Marietta, Georgia; Austin, Texas; Corpus Christi, Texas; Manchester, New Hampshire; Madison, Wisconsin; Augusta, Maine; and Auburn, Alabama.  GDS provides a variety of services to the electric utility industry including power supply planning, generation support services, rates and regulatory consulting, financial analysis, load forecasting and statistical services.  My department, Generation Services, provides fossil and nuclear plant monitoring, plant ownership feasibility studies, plant management audits, production cost modeling and expert testimony on matters relating to plant management, construction, licensing and performance issues in technical litigation and regulatory proceedings.

Q.	WHOM ARE YOU REPRESENTING IN THIS PROCEEDING?

A.	I am representing the Georgia Public Service Commission Public Interest Advocacy Staff (“Staff”).

Q.	WHAT IS YOUR INVOLVEMENT WITH THE VOGTLE 3 AND 4 PROJECT?

A.	I am the Commission’s Independent Construction Monitor (“CM”) for the Vogtle 3 and 4 Project (“Project”).  As such, my duties are to assist the Staff in providing regulatory oversight of all aspects of the Project.  I have presented testimony in the First, Second, Third and Fourth Semi-annual Vogtle Construction Monitoring (“VCM”) proceedings describing the construction monitoring activities, the status of the Project and any concerns or significant issues that I identified.

Q.	WHAT IS YOUR ASSIGNMENT IN THIS PROCEEDING?

My assignment is to present the results of the Staff and CM’s Project oversight from certification of the Project to the present with emphasis on the time period covered by the Fifth Semi-annual Vogtle Construction Monitoring Report, January 1 through June 30, 2011.  I will provide a description of the construction monitoring activities that have occurred since my June 9, 2011 testimony in this docket and describe the current status of the Project.  I will update the Commission on issues that have the potential to impact the schedule or cost of the Project that I have discussed in prior testimony in this docket and identify any new issues that have arisen since the Fourth Semi-annual Vogtle Construction Monitoring filing.  Finally I will make a recommendation regarding the costs submitted by Georgia Power Company (“Company”) for verification and approval.

# II.	Description of Construction Monitoring Activities

Q.	PLEASE DESCRIBE THE CONSTRUCTION MONITORING PROGRAM THAT THE STAFF AND INDEPENDENT CONSTRUCTION MONITOR HAVE IMPLEMENTED TO MONITOR THE CONSTRUCTION OF THE VOGTLE 3 AND 4 PROJECT.

A.	The Staff and the CM continue to be very active in monitoring the Project.  These activities include monthly meetings with Company personnel to discuss Project status and monthly trips to the Vogtle Project site to attend the meeting between the Company and the EPC contractor (Westinghouse / Shaw) and to observe construction activities and progress.  In addition, the CM team has continued its review of the Company’s processing of Project invoices from Westinghouse and Shaw including review of the controlling procedures and reviewing a sample of invoices processed.  Other activities conducted by the Vogtle construction monitoring team include:

- Review of monthly Project status reports issued by the Company;

- Review of monthly Project status reports issued by the Westinghouse – Shaw consortium;

- Review of the Company’s Semi-annual Construction Monitoring Reports;

- Drafting discovery requests for additional information as needed following review of the monthly status reports, semi-annual construction monitoring reports or meetings with the Company;

- Participation in NRC public meetings;

- Review of public correspondence between the Company and the NRC via the NRC website;

- Review of trade articles and journals related to new nuclear power plant development.

Q.	HOW DO YOU KEEP THE STAFF INFORMED ABOUT THE CURRENT STATUS OF THE VOGTLE 3 AND 4 PROJECT?

A.	I discuss the status of the Project and any issues or concerns that have arisen with the Staff in frequent conference calls, meetings and other written communication.  In addition, I submit two monthly reports to the Staff.  At the beginning of each month I submit a Construction Monitor monthly report that describes the current status of the Project and identifies any significant issues or concerns that are new or existing.  In addition, following each monthly EPC meeting, I submit a summary of the meeting and my observations to both the Staff and the Company.  In this report I also include comments and clarifications provided by the Company to ensure that the report is factually accurate.

# III.	Project Status

Q.	PLEASE DESCRIBE THE PROJECT’S CURRENT STATUS?

A.	Significant progress has been made in the key area of licensing with imminent approval of the Design Control Document (DCD) by the NRC and subsequent issuance of the COL anticipated in December 2011 or early 2012.  In addition, construction activities at the site are generally progressing well.  However, as described in more detail later in this testimony, the Project faces significant challenges in achieving commercial operation of Unit 3 in April 2016 and of completing the project within the certified cost.  The Consortium’s most recent monthly status report forecasts commercial operation of Unit 3 on September 6, 2016, some 5 months later than the Guaranteed Substantial Completion Date of April 1, 2016.  It is questionable whether the amount of schedule compression needed to recover the April 1, 2016 date is achievable or the best course of action when considering unknown productivity rates and the economics of such as decision.  While the Project is currently slightly under budget, several potential change notices with significant cost impact remain unresolved.

In addition, many of the issues and concerns that were identified and discussed in the Second, Third and Fourth Semi-annual VCM proceeding have not been resolved at this time.  These issues include:

- Design and fabrication of modules and sub-modules at the Shaw Modular Solutions (“SMS”) facility as required to meet the Project schedule;

- Production of Vogtle specific Certified For Construction (“CFC”) design packages as required to meet the Project schedule.

While progress has been made in these areas during the last six months, the Consortium has not yet demonstrated the ability to produce complete modules and CFC design packages as needed to support the Project schedule.  These challenges are discussed in more detail in Section IV of this testimony.

Q.	PLEASE DESCRIBE THE STATUS OF LICENSING ACTIVITIES FOR THE VOGTLE PROJECT.

A.	As estimated in my testimony in the 4th VCM proceeding, the COL for the Vogtle Project should be issued in December 2011 or early 2012.  An affirmative vote on the AP1000 DCD by the NRC Commissioners is anticipated in the near future which could lead to issuance of the COL in December 2011 or early 2012.  Technical issues described in my testimony in the 4th VCM proceeding regarding shield building loading and containment pressure analyses have been resolved.  There are no outstanding contentions in the Vogtle licensing proceeding.  While interveners have requested that some previously filed contentions be re-opened, it is unlikely that this will delay issuance of the COL.

Q.	PLEASE PROVIDE AN UPDATE ON THE PROJECT SCHEDULE.

A.	The status of the Project with regard to schedule remains unclear at this time.  Prior to issuance of the Consortium’s October 2011 Monthly Status Report, the Project schedule indicated commercial operation of Units 3 and 4 on April 1, 2016 and 2017 respectively.  These dates were achieved by compressing the schedule approximately 2 months to recover earlier Project delays.  In its October 2011 Monthly Status Report, the Consortium revised the Project schedule to indicate commercial operation of Unit 3 on September 6, 2016.  The Company was not consulted and has not agreed to this revised schedule.

Q.	WHAT IS THE BASIS FOR THE CONSORTIUM’S CURRENT SCHEDULE ESTIMATE?

A.	This new projection by the Consortium of Unit 3 COD  by September 6, 2016 is based on starting installation of nuclear island rebar on November 28, 2011 and adding 3 months for rebar installation and First Nuclear Concrete, 48 months for construction and 6 months for startup.  Thus the Consortium, in effect, removed the schedule compression and based the September 2016 date on the original schedule durations.  I note that, as of this writing, installation of nuclear island rebar did not begin on November 28, 2011 and therefore the Project schedule will be further delayed as implied by the most current Consortium Schedule unless steps are taken to recover this delay.

Q.	WHAT IS YOUR OPINION REGARDING SCHEDULE COMPRESSION?

A.	While it is possible that some of the current delay can be recovered through schedule compression, I pointed out in my prior testimony that the Consortium has failed to meet many of the schedule milestones to date and this trend has continued.  Current critical activities such as xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx.  Given the Consortium’s continued inability to meet scheduled milestones to date leads me to question the Consortium’s ability to complete a significant portion of the schedule faster than originally planned.

Q.	HAVE YOU OBSERVED A CHANGE IN THE COMPANY’S POSTURE REGARDING THE SCHEDULE?

A.	Yes I have.  Until now, the Company’s stated position has been that the Project is on track to be completed on schedule by April 1, 2016 for Unit 3 and April 1, 2017 for Unit 4.  When the Project schedule issued in October 2010 showed that commercial operation of Unit 3 had slipped to June 2016, the Company’s position was that they had instructed the Consortium to develop a compressed schedule to recover this delay.  The Company’s testimony in this proceeding reflects a change in their prior position that the current schedule delay can and should be recovered.  On page 6, lines 21 – 23 of their prefiled direct testimony, Company witnesses Ivey and Leach state:

“The Company continues to consider the possibility and potential effect of the DCD schedule delay, and the issues regarding compression of the construction schedule versus the economics and consequences of any potential delay.”

In this statement, the Company recognizes that the risks and benefits of schedule compression must be weighed against the consequences of schedule delay.  Further, during live testimony at the November 21, 2011 hearing on the Company’s direct case Mr. Ivey stated:

“Regardless of these developments, the units remain on track to achieve commercial operation in 2016 and 2017.” (Transcript page 32, lines 9 – 11)

Later in his opening statement Mr. Ivey again stated:

“We remain on track for commercial operation in 2016 and 2017.” (Transcript page 35, line 25 to page 36, line 1)

I believe that the omission of the month of commercial operation in these statements represents a shift in the Company’s position from the Project is on track for Unit 3 commercial operation on April 1, 2016 to a position that the units will be in commercial operation sometime in 2016 and 2017.

Further, in addressing the possibility that the April 1, 2016 date will not be met, Mr. Ivey testified:

“We are considering the pros and cons of revising the compression plan to return the Unit 3 COD to April 1, 2016.  Depending on what actually transpires as we near the finish line on our initial licensing, we must consider how much compression is cost-effective and in the best interest of our customers and our partners.” (Transcript page 33, lines 11 – 16)

By these statements, the Company is acknowledging that commercial operation dates of sometime in 2016 and 2017 are more realistic than the April 1st dates and that schedule compression to recover the April 1st dates needs to be carefully considered, recognizing it may not be the best option.

Q.	IS THIS NEW POSTURE APPROPRIATE?

A.	Yes it is for several reasons.  To be an effective project management tool, a project schedule must be considered realistic and achievable to all parties.  In addition, both the Consortium and the Company must agree on and fully support the Project schedule for the Project to have a high probability of success.  Given the delay in approval of the DCD and subsequent issuance of the COL experienced to date, the likelihood of achieving the April 1st CODs for Units 3 and 4 is becoming more doubtful.  The Company is correct in acknowledging the impact that the current licensing delays are having on the Project schedule.  The Company is also correct in acknowledging that even if recovery of the April 1st dates is possible through schedule compression, that might not be the best path to select.  There are risks as well as benefits to attempting a significant schedule compression.  It is appropriate for the Company to carefully analyze the risks and benefits of an attempt to compress the schedule significantly before it determines a path for the Project to follow.

Q.	PLEASE DESCRIBE THE POSSIBLE BENEFITS AND RISKS OF SCHEDULE COMPRESSION IN MORE DETAIL.

A.	The benefits of successfully compressing the schedule to recover the Guaranteed Substantial Completion Dates of April 1, 2016 and 2017 include lower financing costs that would result from avoiding a schedule delay and lower energy costs due to the low cost energy being available as originally planned.  The risks of attempting a significant schedule compression include the possibility of additional expenditures to fund additional shifts with the inherent inefficiencies without actually achieving the desired schedule compression.  Given the first time nature of the Vogtle 3 and 4 Project, a significantly compressed schedule could result in, among other risks, significant additional cost to staff extra shifts of construction, support and oversight personnel, inefficiencies due to working additional shifts with lower productivity, congestion and unplanned overlap of construction activities, additional rework, and additional regulatory oversight due to increased QA issues.  The impact of these factors could significantly increase the cost of schedule compression and reduce the probability for return to the original schedule for COD.

Q.	PLEASE DESCRIBE THE CURRENT CONSTRUCTION ACTIVITIES AT THE VOGTLE SITE.

A.	Current construction activities at the Vogtle site include safety related activities that are allowed under the Limited Work Authorization and non-safety related activities such as construction of the cooling towers.  These activities continue to generally progress well.  Significant construction activities initiated or completed since my testimony in the 4th VCM proceeding include:

- Completion of the Unit 3 MSE wall;

- Completion of the center section backfill;

- Completion of Unit 3 and 4 circulating water piping;

- Began work on the heavy haul road;

- Completed the Heavy Lift Derrick (HLD) concrete wall;

- Initiated work on the HLD rail;

- Began assembly of HLD components;

- Initiated assembly of CR10;

- Completed assembly of the CA20 platen;

- Began assembly of the CR01 platen;

- Initiated work on the River Water intake structure;

- Initiated work on the 500 kV switchyard.

Q.	WHAT IS THE CURRENT STATUS OF THE PROJECT BUDGET?

A.	As reported in the Company’s 5th VCM report, as of June 30, 2011 Total Project Cost was $xxxxxxxxxxxx  budget with Total Construction and Capital cost $xxxxxxxxxxxx budget and Total Financing Cost $xxxxxxxxxxx budget.  The most recent data available as of October 2011 shows Total Project Cost as $42 million under budget with Total Construction and Capital cost $xxxxxxxxxxxxxx budget and Total Financing Cost $x xxxxxxxxx budget.

EPC capital expenditures continue to be under budget primarily due to the failure of the Consortium to achieve certain milestones in accordance with the Project milestone schedule.  Owners’ capital expenditures are also under budget due to the timing of Project oversight and non-EPC Project activities.  These budget variances are due to timing differences between actual expenditures and the budget and should not impact Total Project Cost.

Q.	WHAT IS THE CURRENT STATUS OF THE TOTAL PROJECT COST FORECAST?

A.	The Company’s current Total Project Cost forecast as of June 2011 is $6.095 billion  which is slightly under the estimate at certification of $6.113 billion.  The most recent forecast to complete the project as of October 2011 is unchanged from the June 2011 forecast.

Q.	DOES THE COMPANY FACE SIGNIFICANT CHALLENGES IN MAINTAINING THE BUDGET FORECAST AT OR BELOW THE CERTIFIED AMOUNT?

A.	Yes, as I discussed in my testimony in the 3rd and 4th VCM proceeding, the Company continues to face significant challenges in maintaining the Project forecast at or below the certified amount.  A possible schedule delay as discussed above would impact the financing cost of the Project.  In addition, the Company’s forecast does not include many potential change orders that could significantly impact the direct construction cost of the Project.  I identified some of these potential change orders in my testimony in the Third and Fourth Semi-annual VCM proceeding.  In addition to the list of potential changes provided in my testimony in the 4th VCM proceeding, the Consortium has submitted the following additional Potential Change Notices:

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx – Contractor identified a potential change due to the xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx – Contractor identified a potential change due to implementation of the xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx

xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx.

xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxx.  These potential changes are shown below:

- Japan Earthquake – Consortium identified a potential change for impacts to suppliers from the Japan earthquake;

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx – Consortium identified a potential change due to the xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxxxx – Consortium identified a potential change for xxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx - Consortium identified potential cost impacts for xxxxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx - Consortium identified potential cost impacts xxxxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxx – Consortium has sent a potential change order to cover xxxxxxxxxxxxxxxxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx – Consortium has sent a potential change order to cover xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx – Consortium identified potential cost impacts for xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx;

- xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx - Consortium has sent a potential change notice due to weather delays that affect excavation.

In addition, the Company has identified “xxxxxxxxxxxxxxxxxxxxxxxxxxxx” as a developing issue for which there is potential for the Consortium to issue a change request.

Q.	HAS THE COMPANY MADE PROGRESS SINCE THE 4TH VCM PERIOD TO RESOLVE THESE POTENTIAL CHANGE NOTICES?

A.	The Company has made little progress in resolving the potential changes in the six months since my last testimony.  xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx.  When asked at the November 21, 2011 hearing to provide an update to the Commission on the status of these changes, Mr. Ivey responded:

Progress has been slow, we don't have a great deal more detail today on some of these potential changes than we had at the time of the fourth VCM, indeed in the filing of the fifth. (Transcript page 59, lines 1 – 4)

Q.	WHY IS IT IMPORTANT THAT THESE ISSUES BE RESOLVED?

A.	Some of these potential change orders could have a significant impact on the Project cost.  The forecast cost provided in the Company’s testimony does not include the possible cost impact of these potential change notices.  Until the magnitude of the costs associated with these potential change orders and the responsibility for these costs is known, the forecast cost for the Project is uncertain.  Uncertainty in the Project cost inhibits Staff’s ability to conduct the meaningful economic analyses that Staff and the Commission require.  In addition, until these commercial issues are resolved, it will be difficult for the Company and Consortium to agree upon and fully support the Project schedule.  The cause for Project delays, the responsibility for the delays and the cost of the delays need to be resolved before all parties can agree on a schedule.

Q.	THE COMPANY HAS INDICATED IN THE 5TH VCM REPORT THAT THE BUDGET FOR OVERSIGHT WILL BE INCREASED BY $xxxxxxxxxx.  WHAT IS YOUR OPINION OF THIS INCREASE?

A.	As I have reported in my monthly reports to this Commission, the Company has been actively involved in providing oversight of the Project.  The Company has provided its expertise to the Consortium in certain areas.  Company personnel have held the Consortium accountable for their commitments.  However, the Company has indicated in this reporting period that additional oversight is needed due to gaps in the Consortium’s performance.  In addition, 10CFR50, Appendix B, which specifies the quality assurance requirements for construction of a nuclear power plant, is clear that the Company is ultimately responsible to ensure that the quality assurance requirements specified in Appendix B are met.  In my opinion the Company is in the best position to determine the amount of oversight needed to meet these requirements.

Q.	IF ADDITIONAL OVERSIGHT IS REQUIRED BECAUSE OF POOR PERFORMANCE BY THE CONSORTIUM, WHO SHOULD BEAR THE COST FOR THIS ADDITIONAL OVERSIGHT?

A.	The Staff believes ratepayers should not pay for additional Company oversight that is required due to continuing poor performance by the Consortium.  Although the Company may determine that additional oversight is warranted for it to fulfill its duty under NRC regulations to successfully execute the Project, responsibility for payment for the additional oversight is yet to be determined.  The Company should avail itself of all recourses and legal remedies outlined in the EPC agreement to recoup these additional costs from the Consortium.  The Company has indicated that this is their intent.

# IV.	OTHER Issues Potentially Impacting Project Schedule and/or Cost

Q.	PLEASE PROVIDE AN UPDATE TO THE COMMISSION ON THE ISSUES RELATED TO QUALITY ASSURANCE, DESIGN AND FABRICATION OF  MODULES AND SUBMODULES AT THE SHAW MODULAR SOLUTIONS FACILITY.

A.	Issues related to quality assurance, design, material and fabrication problems at the Shaw Modular Solutions (SMS) facility were discussed in my 3rd and 4th VCM testimony.  SMS has been the subject of significant management attention by both Consortium and Company senior management.  Corrective actions have been identified and progress has been made in resolving the issues that delayed the design and fabrication of modules.  However, the ability of SMS to provide complete high quality modules to meet the Project schedule remains a significant concern.  According to the module delivery schedule as of November 11, 2011, xxxx of xx scheduled modules have been delivered to the site.  However, the schedule for module deliveries shown in a prior Consortium Monthly Status Report dated August 31, 2011 indicates that xx modules were scheduled to be delivered to the site.  xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx .  However, now that DCD approval and receipt of the COL are imminent, SMS must meet the required production rate of high quality modules or the Project schedule will be impacted.

Q.	PLEASE DESCRIBE THE ISSUE RELATED TO DESIGN FINALIZATION.

A.	Finalization of the detailed Vogtle specific AP1000 design culminating in issuance of Certified For Construction (CFC) design packages for the Project remains a concern.  As described in my prior testimony, the plan for the Project is to have all engineering deliverables (construction drawings, specifications, etc.) for construction available xxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx.

In October 2011, xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxx.  For example, the cumulative number of CFC packages planned for completion in October 2011 as shown in the September 2011 Consortium Monthly Status Report of xx was xxxxxxxxxxxx planned CFC packages in the Consortium’s October 2011 report.  As with production of modules, development and issuance of CFC packages has received significant attention from Consortium and Company management.  Progress has been made in resolving the issues that have been xxxxxxxxxxxxxxxxx of the CFC packages.  However, the required production of CFC packages increases rapidly from xxxxxxxxxxxxxxxxxxxxxxxxxxxxx to approximately xx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx xxxxxxxxxx.

# V	Verification and Approval of Costs

Q.	WHAT IS STAFF’S RECOMMENDATION CONCERNING VERIFICATION AND APPROVAL OF THE COSTS REQUESTED BY THE COMPANY?

A.	Subject to the recommendations of other Staff witnesses, Staff recommends that the costs requested by the Company in this Fifth Semi-annual Review be verified and approved by the Commission.

Q.	DOES THIS CONCLUDE YOUR TESTIMONY?

A.	Yes it does.

EXHIBIT STF-WRJ-1

Resume of William R. Jacobs, Jr.

EDUCATION:	Ph.D., Nuclear Engineering, Georgia Tech 1971

MS, Nuclear Engineering, Georgia Tech 1969

BS, Mechanical Engineering, Georgia Tech 1968

ENGINEERING REGISTRATION:	Registered Professional Engineer

PROFESSIONAL MEMBERSHIP:	American Nuclear Society

EXPERIENCE:

Dr. Jacobs has over thirty-five years of experience in a wide range of activities in the electric power generation industry.  He has extensive experience in the construction, startup and operation of nuclear power plants.  While at the Institute of Nuclear Power Operation (INPO), Dr. Jacobs assisted in development of INPO’s outage management evaluation group.  He has provided expert testimony related to nuclear plant operation and outages in Texas, Louisiana, South Carolina, Florida, Wisconsin, Indiana, Georgia and Arizona.  He currently provides nuclear plant operational monitoring services for GDS clients.  He is assisting the Florida Office of Public Counsel in monitoring the development of four new nuclear units in the State of Florida.  He provides testimony before the Florida Public Service Commission concerning the prudence of expenditures for these nuclear units.  He has assisted the Georgia Public Service Commission staff in development of energy policy issues related to supply-side resources and in evaluation of applications for certification of power generation projects and assists the staff in monitoring the construction of these projects.  He has also assisted in providing regulatory oversight related to an electric utility’s evaluation of responses to an RFP for a supply-side resource and subsequent negotiations with short-listed bidders.  He has provided technical litigation support and expert testimony support in several complex law suits involving power generation facilities.  He monitors power plant operations for GDS clients and has provided testimony on power plant operations and decommissioning in several jurisdictions.  Dr. Jacobs has provided testimony before the Georgia Public Service Commission, the Public Utility Commission of Texas, the North Carolina Utilities Commission, the South Carolina Public Service Commission, the Iowa State Utilities Board, the Louisiana Public Service Commission, the Florida Public Service Commission, the Indiana Regulatory Commission, the Wisconsin Public Service Commission, the Arizona Corporation Commission and the FERC.

A list of Dr. Jacobs’ testimony is available upon request.

1986-Present	GDS Associates, Inc.

As Vice-President, Dr. Jacobs directs GDS' nuclear plant monitoring activities and has assisted clients in evaluation of management and technical issues related to power plant construction, operation and design. He has evaluated and testified on combustion turbine projects in certification hearings and has assisted the Georgia PSC in monitoring the construction of the combustion turbine projects.  Dr. Jacobs has evaluated nuclear plant operations and provided testimony in the areas of nuclear plant operation, construction prudence and decommissioning in nine states. He has provided litigation support in complex law suits concerning the construction of nuclear power facilities.

1985-1986	 Institute of Nuclear Power Operations (INPO)

Dr. Jacobs performed evaluations of operating nuclear power plants and nuclear power plant construction projects.  He developed INPO Performance Objectives and Criteria for the INPO Outage Management Department.  Dr. Jacobs performed Outage Management Evaluations at the following nuclear power plants:

	Connecticut Yankee - Connecticut Yankee Atomic Power Co.

	Callaway Unit I - Union Electric Co.

	Surry Unit I - Virginia Power Co.

	Ft. Calhoun - Omaha Public Power District

	Beaver Valley Unit 1 - Duquesne Light Co.

During these outage evaluations, he provided recommendations to senior utility management on techniques to improve outage performance and outage management effectiveness.

1979-1985	Westinghouse Electric Corporation

As site manager at Philippine Nuclear Power Plant Unit No. 1, a 655 MWe PWR located in Bataan, Philippines, Dr. Jacobs was responsible for all site activities during completion phase of the project.  He had overall management responsibility for startup, site engineering, and plant completion departments.  He managed workforce of approximately 50 expatriates and 1700 subcontractor personnel.  Dr. Jacobs provided day-to-day direction of all site activities to ensure establishment of correct work priorities, prompt resolution of technical problems and on schedule plant completion.

Prior to being site manager, Dr. Jacobs was startup manager responsible for all startup activities including test procedure preparation, test performance and review and acceptance of test results.  He established the system turnover program, resulting in a timely turnover of systems for startup testing.

As startup manager at the KRSKO Nuclear Power Plant, a 632 MWE PWR near Krsko, Yugoslavia, Dr. Jacobs' duties included development and review of startup test procedures, planning and coordination of all startup test activities, evaluation of test results and customer assistance with regulatory questions.  He had overall responsibility for all startup testing from Hot Functional Testing through full power operation.

1973 - 1979	NUS Corporation

As Startup and Operations and Maintenance Advisor to Korea Electric Company during startup and commercial operation of Ko-Ri Unit 1, a 595 MWE PWR near Pusan, South Korea, Dr. Jacobs advised KECO on all phases of startup testing and plant operations and maintenance through the first year of commercial operation.  He assisted in establishment of administrative procedures for plant operation.

As Shift Test Director at Crystal River Unit 3, an 825 MWE PWR, Dr. Jacobs directed and performed many systems and integrated plant tests during startup of Crystal River Unit 3. He acted as data analysis engineer and shift test director during core loading, low power physics testing and power escalation program.

As Startup engineer at Kewaunee Nuclear Power Plant and Beaver Valley, Unit 1, Dr. Jacobs developed and performed preoperational tests and surveillance test procedures.

1971 - 1973	Southern Nuclear Engineering, Inc.

Dr. Jacobs performed engineering studies including analysis of the emergency core cooling system for an early PWR, analysis of pressure drop through a redesigned reactor core support structure and developed a computer model to determine tritium build up throughout the operating life of a large PWR.

SIGNIFICANT CONSULTING ASSIGNMENTS:

Georgia Public Service Commission – Selected as the GPSC’s Independent Construction Monitor for the Plant Vogtle 3 and 4 nuclear construction projects.  Assists the Commission staff in providing oversight of all aspects of the Plant Vogtle 3 and 4 project.  Provides testimony in the semi-annual hearing before the GPSC on the Vogtle project.

South Carolina Office of Regulatory Staff – Assisted the South Carolina Office of Regulatory Staff in evaluation of South Carolina Electric and Gas’ request for certification of two AP1000 nuclear power plants at the V.C. Summer site.

Florida Office of Public Counsel – Assists the Florida Office of Public Counsel in monitoring the development of four new nuclear power plants in Florida including providing testimony on the prudence of expenditures.

East Texas Electric Cooperative – Represented ETEC on the management committee of the Plum Point Unit 1 a 650 Mw coal-fired plant under construction in Osceola, Arkansas and represents ETEC on the management committee of the Harrison County Power Project, a 525 Mw combined cycle power plant located near Marshall, Texas.

Arizona Corporation Commission – Evaluated operation of the Palo Verde Nuclear Generating Station during the year 2005.  Included evaluation of 11 outages and providing written and oral testimony before the Arizona Corporation Commission.

Citizens Utility Board of Wisconsin – Evaluated Spring 2005 outage at the Kewaunee Nuclear Power Plant and provided direct and surrebuttal testimony before the Wisconsin Public Service Commission.

Georgia Public Service Commission - Assisted the Georgia PSC staff in evaluation of Integrated Resource Plans presented by two investor owned utilities.  Review included analysis of purchase power agreements, analysis of supply-side resource mix and review of a proposed green power program.

State of Hawaii, Department of Business, Economic Development and Tourism – Assisted the State of Hawaii in development and analysis of a Renewable Portfolio Standard to increase the amount of renewable energy resources developed to meet growing electricity demand.  Presented the results of this work in testimony before the State of Hawaii, House of Representatives.

Georgia Public Service Commission - Assisted the Georgia PSC staff in providing oversight to the bid evaluation process concerning an electric utility’s evaluation of responses to a Request for Proposals for supply-side resources.  Projects evaluated include simple cycle combustion turbine projects, combined cycle combustion turbine projects and co-generation projects.

Millstone 3 Nuclear Plant Non-operating Owners – Evaluated the lengthy outage at Millstone 3 and provided analysis of outage schedule and cost on behalf of the non-operating owners of Millstone 3.  Direct testimony provided an analysis of additional post-outage O&M costs that would result due to the outage.  Rebuttal testimony dealt with analysis of the outage schedule.

H.C. Price Company – Evaluated project management of the Healy Clean Coal Project on behalf of the General Contractor, H.C. Price Company.  The Healy Clean Coal Project is a 50 megawatt coal burning power plant funded in part by the DOE to demonstrate advanced clean coal technologies.  This project involved analysis of the project schedule and evaluation of the impact of the owner’s project management performance on costs incurred by our client.

Steel Dynamics, Inc. – Evaluated a lengthy outage at the D.C. Cook nuclear plant and presented testimony to the Indiana Utility Regulatory Commission in a fuel factor adjustment case Docket No. 38702-FAC40-S1.

Florida Office of Public Counsel - Evaluated lengthy outage at Crystal River Unit 3 Nuclear Plant. Submitted expert testimony to the Florida Public Service Commission in Docket No. 970261-EI.

United States Trade and Development Agency - Assisted the government of the Republic of Mauritius in development of a Request for Proposal for a 30 MW power plant to be built on a Build, Own, Operate (BOO) basis and assisted in evaluation of Bids.

Louisiana Public Service Commission Staff - Evaluated management and operation of the River Bend Nuclear Plant. Submitted expert testimony before the LPSC in Docket No. U-19904.

U.S. Department of Justice - Provided expert testimony concerning the in-service date of the Harris Nuclear Plant on behalf of the Department of Justice U.S. District Court.

City of Houston - Conducted evaluation of a lengthy NRC required shutdown of the South Texas Project Nuclear Generating Station.

Georgia Public Service Commission Staff - Evaluated and provided testimony on Georgia Power Company's application for certification of the Intercession City Combustion Turbine Project - Docket No. 4895-U.

Seminole Electric Cooperative, Inc. - Evaluated and provided testimony on nuclear decommissioning and fossil plant dismantlement costs - FERC Docket Nos. ER93-465-000, et al.

Georgia Public Service Commission Staff - Evaluated and prepared testimony on application for certification of the Robins Combustion Turbine Project by Georgia Power Company - Docket No. 4311-U.

North Carolina Electric Membership Corporation - Conducted a detailed evaluation of Duke Power Company's plans and cost estimate for replacement of the Catawba Unit 1 Steam Generators.

Georgia Public Service Commission Staff - Evaluated and prepared testimony on application for certification of the McIntosh Combustion Turbine Project by Georgia Power Company and Savannah Electric Power Company - Docket No. 4133-U and 4136-U.

New Jersey Rate Counsel - Review of Public Service Electric & Gas Company nuclear and fossil capital additions in PSE&G general rate case.

Corn Belt Electric Cooperative/Central Iowa Power Electric Cooperative - Directs an operational monitoring program of the Duane Arnold Energy Center (565 Mwe BWR) on behalf of the non-operating owners.

Cities of Calvert and Kosse - Evaluated and submitted testimony of outages of the River Bend Nuclear Station - PUCT Docket No. 10894.

Iowa Office of Consumer Advocate - Evaluated and submitted testimony on the estimated decommissioning costs for the Cooper Nuclear Station - IUB Docket No. RPU-92-2.

Georgia Public Service Commission/Hicks, Maloof & Campbell - Prepared testimony related to Vogtle and Hatch plant decommissioning costs in 1991 Georgia Power rate case - Docket No. 4007-U.

City of El Paso - Testified before the Public Utility Commission of Texas regarding Palo Verde Unit 3 construction prudence - Docket No. 9945.

City of Houston - Testified before Texas Public Utility Commission regarding South Texas Project nuclear plant outages - Docket No. 9850.

NUCOR Steel Company - Evaluated and submitted testimony on outages of Carolina Power and Light nuclear power facilities - SCPSC Docket No. 90-4-E.

Georgia Public Service Commission/Hicks, Maloof & Campbell - Assisted Georgia Public Service Commission staff and attorneys in many aspects of Georgia Power Company's 1989 rate case including nuclear operation and maintenance costs, nuclear performance incentive plan for Georgia and provided expert testimony on construction prudence of Vogtle Unit 2 and decommissioning costs of Vogtle and Hatch nuclear units - Docket No. 3840-U.

Swidler & Berlin/Niagara Mohawk - Provided technical litigation support to Swidler & Berlin in law suit concerning construction mismanagement of the Nine Mile 2 Nuclear Plant.

Long Island Lighting Company/Shea & Gould - Assisted in preparation of expert testimony on nuclear plant construction.

North Carolina Electric Membership Corporation - Prepared testimony concerning prudence of construction of Carolina Power & Light Company's Shearon Harris Station - NCUC Docket No. E-2, Sub537.

City of Austin, Texas - Prepared estimates of the final cost and schedule of the South Texas Project in support of litigation.

Tex-La Electric Cooperative/Brazos Electric Cooperative - Participated in performance of a construction and operational monitoring program for minority owners of Comanche Peak Nuclear Station.

Tex-La Electric Cooperative/Brazos Electric Cooperative/Texas Municipal Power Authority (Attorneys - Burchette & Associates, Spiegel & McDiarmid, and Fulbright & Jaworski) - Assisted GDS personnel as consulting experts and litigation managers in all aspects of the lawsuit brought by Texas Utilities against the minority owners of Comanche Peak Nuclear Station.